WEEKLY FIRE PUMP CHURN TEST

FACILITY:  	______________________________		DATE:  _______________________

TEST COMPLETED BY:  ________________________________________________________

Circle one below

| - Call the fire alarm monitoring company and put the fire system in test. | YES | NO | N/A |
| --- | --- | --- | --- |
| - Find a drain in the system and open slowly until the pressure starts to drop. Listen/look for the jockey pump (pressure maintenance pump) to turn on. Once that happens, close the system valve and let the pressure build up until the pump shuts off. | YES | NO | N/A |
| - Open the system drain again, but this time when the jockey pump (pressure maitnenace pump) turns on, open the valve more so the pressure continues to drop.. Leave the valve open until the fire pump turns on and once that happens, close the system drain valve. | YES | NO | N/A |
| - Find the casing relief valve on the discharge side of the fire pump and make sure that it is flowing water. This is what keeps the fire pump cool while chum test is in progress. | YES | NO | N/A |
| - Make sure the packing glands have a slow and steady drip so the pump shaft is lubricated. | YES | NO | N/A |
| - If the fire pump is set up with a timer, let the pump run until the timer automatically shuts off. If the fire pump is set up, manual shut down will only let the pump run for ten minutes and turn off manually. | YES | NO | N/A |
| - Reset fire alarm panel and make sure all the alarms clear and everything is normal. | YES | NO | N/A |
| - Call the fire alarm monitoring company and put the fire alarm back in service. | YES | NO | N/A |
| - Weekly Visual Inspection of fire pump assembly operating and physical condition. |  |  |  |

Suction Pressure  _______________		Discharge Pressure _____________________________

Run Time ______________________	Monthly Circuit/Breaker Exercise __________________

COMMENTS:  ______________________________________________________________________________

__________________________________________________________________________________________

____________________________________________________________________________________________________________________________________________________________________________________